## Slide 1
GridSweep:
Using Synchro-Waveforms to Probe Distribution Grid Stability from 120V Outlets
Alex McEachern, IEEE Life Fellow

## Slide 2: GridSweep is a new type of grid research instrument.
4-year $4M U.S. Dept of Energy project
100% open-source
  Hardware, firmware, software, data
  LBNL has a loaner fleet of GridSweep instruments available.
Two independent grid edge functions:
  Synchroprobing the grid via 120-volt outlets.
  Recording voltage synchrowaveforms on 120-volt outlets, at parts-per-billion resolution.

## Slide 3: GridSweep applications
Using only grid edge (120-volt outlet) measurements:
Confirmed: Measure risk of instability on IBR-intensive feeders.
Research opportunity: Microdisturbances: Map real-time grid configuration. Detect grid ignition faults.
Research opportunity: Detect substation cyberattack rehearsals using source impedance changes

## Slide 4: New ideas about grid impedances
Traditional grid measurements: voltages, currents, power flows.
  Source impedance measurements were generally limited to arc-flash risks and protection device ratings. But now other concerns are emerging.
Traditional source impedance: transmission/distribution transformers & lines, and to a lesser extent generators.
  But now we have distributed generation and reconfigurable grids (and negative impedance loads like EV chargers, AI data centers, etc.)
Traditional source impedance: 50/60 Hz, or maybe up to 3 kHz(?)
  But now we have important sub-synchronous (say, 1 Hz – 40 Hz) impedance concerns for stability and substation cyberattack detection
???
What about R(f)? L(f)?
What if the load impedance is negative?

## Slide 6: Measure risk of instability: active grid probing methods
 |  | Source | Stimulus | Measurement devices | Measurement resolution | Noise extraction method
1980s- |  | Chief Joseph Brake | 1 GW impulse | Fault recorders | 1000 ppm 0.1% | None
2015- |  | Grid Thumper | 1 MW impulse | microPMUs | 10 ppm 0.001% | Time-synchronous demodulation
2022- |  | GridSweep | 1 kW swept sine | GridSweep | 6 ppb 0.0000006% | Single frequency vector-synchronous demodulation

## Slide 7: Measure risk of instability: GridSweep results for IBR’s

## Slide 8: “Microdisturbances for grid state measurement” A proposed new application for grid edge synchrowaveforms.
Red: Medium voltage Blue: Grid edge voltage (120V)
Source of graph:
Prof. Hamed Mohsenian-Rad
U.C. Riverside

## Slide 9: “Microdisturbance” concept & application
Proposed definition of “microdisturbance”:
any power quality disturbance that is detectable, but is too tiny to disrupt or damage any sensitive load.
Microdisturbance #2
Microdisturbance #1
Medium voltage RMS
Medium voltage RMS
Grid edge voltage RMS (120V)
Grid edge voltage RMS (120V)
Microdisturbance #3
Red: Medium voltage Blue: Grid edge voltage (120V)
Cheap & simple & easy-to-install sensors should be developed.
Grid state estimation consists of correlation between simultaneously observed grid-edge microdisturbances, observed at a population of locations around the grid.
What does it take for real-time corellation?
Source of graphs:
Prof. Hamed Mohsenian-Rad
U.C. Riverside

## Slide 10: Microdisturbance correlation: Computing & comms required for ‘n’ GridSweep-scale 120-volt sensors
 |  | Computer | Cost | Calculation power: megaFLOPs | Ethernet comms speed: Megabytes/sec
2024 |  | Powerful desktop workstation | US$5k | 1 x 103 | 1 x 102
2025 |  | Re-purposed Artificial Intelligence workstation | US$50k | 5 x 109 | 2 x 104
Pairs of sensors to be correlated: (n2-n)/2 pairs Data comms per sensor: 10-1 megabytes/sec
Real-time correlation computing power required per pair of sensors: ~ 4 x 10-2 megaFLOPs
Example: n=100 sensors Pairs of sensors ~ 1 x 104 4 x 102 megaFLOPS 1 x 102 megabytes/sec
Example: n=40,000 sensors Pairs of sensors ~ 1 x 109 4 x 107 megaFLOPS 4 x 103 megabytes/sec

## Slide 11: Three calls for action!

## Slide 12: Calls for action! (1)
Need FREE real-world grid edge synchrowaveform data?
  Download from ORNL’s GESL. Hundreds of gigabytes available, from a variety of distribution grids, complete with metadata.
GESL.ORNL.GOV

## Slide 13: Calls for action! (2)
Have an interesting idea? LBNL has a fleet of GridSweep instruments specifically for loaning out to National Labs, universities, utilities…
GridSweep data – 8-hour, 5Hz - 40Hz ,heat map at U.C. Riverside

## Slide 14: Calls for action! (3)
ALEX@MCEACHERN.com
+1-510-295-8264
Discuss a grid-mapping microdisturbance project? I can connect and advise. (In my opinion, this is the important opportunity.)
Discuss measurements for detecting rehearsals of substation cyberattacks? Private discussion.

## Slide 15
Thank you.
Alex McEachern, IEEE Life Fellow
ALEX@MCEACHERN.com
+1-510-295-8264