## Slide 1
Improve grid edge awareness with continuous waveform recording
Richard D. Kirby, Senior Engineer

## Slide 2: Continuous waveform streaming and recording – DFRs, PQMs, and PMs
14.4 ksps
3 ksps
3 ksps
SEL-T35
PM WMU
PQM WMU
DFR WMU
Controller
CWR PC
Software application
Notes: DFR WMU: DFR CT/PT cards for 3 ksps continuous waveform streaming PQM WMU : Power Quality and Revenue Meter combines revenue and PQ with 3 ksps continuous waveform streaming
PM WMU : Power Monitor measures ac and dc power with conversion with 14.4 ksps continuous waveform streaming

## Slide 3: Integrate various measurement rates from relays, meters, PMUs, and WMUs
WMU
CWR PC
Software application

## Slide 4: Triggerless recording captures every disturbance
Recording device
Trigger
Duration
Traditional
Continuous waveform recording
Use case 1

## Slide 5: Trigger dependent systems can miss events
Traditional
Continuous recording

## Slide 6: Capture voltage-induced flicker missed by traditional monitoring

## Slide 7: Increase visibility of power system dynamics
Use case 2

## Slide 8: AI training runs create large load changes that can induce resonance
15 MW
150 MW
Small city
10
20
30
40
50
Time (s)

## Slide 9: Identify equipment failure early
Use case 3
Notes: Coming soon: Diagram or set of figures that demonstrate precursor events often identify failures early

## Slide 10: Three-second SCADA misses transient
SCADA
0
100
200
300
9,200
8,800
8,400
8,000
7,600
2:VARMS.SCADA
Time (ms)
RMS voltage

## Slide 11: 60 messages/second PMU data starts to see transient
PMU
2:VARMS.SCADA
3:VARMS.PMU
0
100
200
300
RMS voltage
9,200
8,800
8,400
8,000
7,600
Time (ms)

## Slide 12: Relay event reports approximate transient
16 samples per cycle
2:VARMS.SCADA
3:VARMS.PMU
4:VARMS.16SPC
0
100
200
300
RMS voltage
9,200
8,800
8,400
8,000
7,600
Time (ms)

## Slide 13: Continuous recording at 14.4 ksps captures peak and ringing
14.4 ksps
2:VARMS.SCADA
3:VARMS.PMU
4:VARMS.16SPC
5:VARMS.T35
0
100
200
300
RMS voltage
9,200
8,800
8,400
8,000
7,600
Time (ms)

## Slide 14: Visualize hours of transients on one timeline

## Slide 15: Software derived PMU and SCADA metering applications
Quantity | Description
V, I, and Φ | 1 cycle rms, fundamental
Frequency | 1/2 cycle frequency
P, Q, and S | 1 cycle rms, fundamental
Symmetrical components | 1 cycle rms
SSO/SSR | 5 – 45 Hz
Harmonics | 25th or 100th
PMU and SCADA metering
Continuous waveform
recording

## Slide 16: Consider network bandwidth and storage when streaming and recording ksps data
Model | Sample rate (ksps) | Channels | Network bandwidth (kbps) | Storage per channel (GB per day)
Meter | 3.0 | 6 | 600 | 1
DFR | 3.0 | 96 | 9,700 | 1
Monitor | 14.4 | 17 | 11,100 | 5

## Slide 17
THANK YOU
Richard D. Kirby
Richard_Kirby@selinc.com
+1.509.334.8150